## Diagnostic Checklist
Mawdsleys Pump Services – “Why Isn’t My Pump Working?” Diagnostic Checklist
Identify which pattern matches your pump, then work through its checks in order. Call us immediately at any High risk step.
01179548030 | enquiries@mawdsleysber.com
Step | Check | What To Look For | Likely Cause | Risk Level | DIY Safe? | Status (fill in)
PATTERN 1 – PUMP WON'T TURN ON AT ALL
1 | Confirm power at the isolator/fused spur | Isolator position, indicator light, blown local fuse | Isolator off or fuse blown | Low | Yes
2 | Check the consumer unit / fuse board | Tripped MCB or tripped RCD on the pump circuit | Overload or earth leakage fault | Medium | Yes – reset once only
3 | Inspect the float switch (sump/sewage/borehole tank) | Float stuck, tangled cable, jammed in debris | Float switch failure – most common no-start cause | Low | Yes
4 | Check the water/well level | Level below the pump's minimum intake point | Low-level cut-out preventing start (protection working) | Low | Yes
PATTERN 2 – PUMP RUNS BUT NO WATER COMES OUT
5 | Listen and check water level at the same time | Motor running normally but no discharge flow | Airlock, or water level below intake causing cavitation | High | No – isolate and call us
6 | Inspect the intake strainer (where accessible) | Debris, sediment or biofilm blocking the intake | Clogged intake or jammed impeller | Medium | No – call us
7 | Check the discharge line | Kinked, frozen or visibly blocked pipe/hose | Restricted discharge stopping flow | Medium | Yes – clear visible kinks only
8 | Check the check (non-return) valve | Water draining back down the pipe between cycles | Failed or stuck check valve | Medium | No – call us
PATTERN 3 – PUMP SHORT-CYCLES (ON/OFF TOO OFTEN)
9 | Tap the pressure tank top to bottom | Solid ‘thud’ throughout instead of hollow at the top | Waterlogged pressure tank / failed bladder | Medium | Yes – test only, no dismantling
10 | Check the tank's air charge at the Schrader valve | Air pressure below ~2 psi under the pump's cut-in setting | Lost air charge in the tank | Low | Yes – with a tyre gauge
11 | Check for water spraying from the air valve | Water present at the air valve when pressed | Ruptured tank bladder | Medium | No – call us
12 | Check for slow drips or leaks in the pipework | Any dripping fitting, tap or joint | System leak bleeding away pressure | Low | Yes – visual check
PATTERN 4 – PUMP RUNS CONTINUOUSLY / WEAK FLOW
13 | Compare current flow to normal performance | Noticeably reduced pressure or flow at the outlet | Worn impeller/stages, or clogged filter | Low | Yes – observation only
14 | Check inline filters or strainers | Visible debris or scale build-up | Partial blockage reducing flow | Low | Yes
15 | Check recent changes in demand or water level | New appliances added, or seasonal drawdown of well/borehole | Pump undersized for current demand or depth | Medium | No – call us for resizing advice
16 | Check for continuous running with falling pressure | Pump never switches off; pressure keeps dropping | Downstream leak | Medium | No – call us
How to use this sheet:
1. Start by matching your symptom to one of the four pattern headings above, then work through only that section.
2. Column G (Status) has a drop-down – update it as you work through each check.
3. If your pump is running but producing no water, isolate it at the earliest safe opportunity – dry-running can damage a submersible motor within minutes to hours.
4. Never reset a tripped RCD or MCB more than once. A repeat trip indicates a genuine electrical fault (BS 7671:2018+A3:2024; Total Skills UK, 2026).
5. This checklist is general guidance and does not replace inspection by a qualified engineer.

## Maintenance Log
Pump Maintenance Log
Keep a running record – inspection every 6 months for domestic units and every 3 months for commercial/sewage duty pumps is a typical starting point.
01179548030 | enquiries@mawdsleysber.com
Date | Pump / Location | Task Performed | Performed By | Findings | Parts Replaced | Next Service Due | Notes
2026-01-15 | Borehole pump – pump house | 6-monthly inspection: pressure tank air charge, check valve, flow test | Mawdsleys Engineer | Pressure tank air charge slightly low – recharged to spec | None | 2026-07-14 | No further action required
Column G calculates automatically as 180 days after the date in column A (edit the formula for a different interval). Row 5 (highlighted) is a worked example – overwrite it.
Formulas:
Next Service Due = [Date]+180

## Reference & Contact
Reference Guide & Contact Details
Sources cited in the accompanying blog post, and how to reach Mawdsleys Pump Services.
01179548030 | enquiries@mawdsleysber.com
Failure Pattern | Typical Cause
Won't turn on – electrical | RCD/MCB trips on outdoor and submersible pump circuits are required under BS 7671
Won't turn on – float switch | Most frequent single cause of sump pump non-start
Runs but no water – airlock | Trapped air at the impeller blocks flow even though the motor runs normally
Runs but no water – low level | Pump pulls air instead of water once the static level drops below the intake
Runs but no water – clog | Debris jams the impeller vanes while the motor keeps turning
Dry-running damage | A submersible motor without cooling water flow can be damaged within minutes to hours
Short-cycling – pressure tank | A waterlogged tank / failed bladder is the leading cause of short cycling
Short-cycling – pressure switch | A clogged or faulty pressure switch sends incorrect on/off signals
Continuous running / weak flow | Impeller wear, clogging, or an undersized pump reduce delivered flow over time
Borehole compliance | Private water supplies including boreholes fall under statutory regulation in England
Contact Mawdsleys Pump Services
• 24/7 emergency support – speed of response is one of our core service standards.
• Submersible pump specialists – fault-finding, repair, replacement and planned maintenance.
• Reliable. Rapid. Informative. – clear communication at every stage of the job.
• See our Google Reviews for verified customer feedback.